## Slide 1: Product Technical Factory Training
Presented by: Sagar Shah, TPM

## Slide 2: Agenda
  Introduction
  Product Overview
  Installation
  Features & Benefits (USPs)
  Applications

## Slide 3: Steam Distribution
Direct Room Application
Duct Application Distributors
xSD
Mini SAM-e
Remote Mounted or Space Model
SAM-e

## Slide 4: Condair SAM-e
Short Absorption Manifolds

## Slide 5: Why SAM-e?
Why SAM-e
Short Absorption Manifold
Easy to install; made with 304 SST
Lower cost & easier to install than multiple LS distributors
Can be used with atmospheric steam or pressure (boiler) steam
10 years standard warranty
Your AHU manufacturers like it!

## Slide 6: Product Overview
Short Absorption Manifolds

## Slide 7: Product Overview
SAM-e Components
Mounting Frame
Steam Tubes
Header
Inlet Adapter
Condensate Drain

## Slide 8: Product Overview
SAM-e Header
Width
Spacing
9.0”
8.7”
Fits ducts 18” – 144” wide
3”, 6”, 9”, 12” spacing
Atmospheric or pressure steam
Atmospheric up to 800lbs/hr
Pressure up to 3200lbs/hr

## Slide 9: Product Overview
SAM-e Header 801-1200 lb/hr
Atmospheric steam
3”, 6”, 9” or 12” spacing
Fits ducts 42” – 144
Width
Spacing
9.0”
8.7”

## Slide 10: Product Overview
SAM-e Steam Tubes
Lengths from 6” to 132”
4 Types:
Type A: 15 lbs/hr
Type B: 35 lbs/hr
Type B+: 55 lbs/hr
Type C: 75 lbs/hr
Length

## Slide 11: Product Overview
How SAM-e Steam Tubes Work
Airflow
Hot Steam
Condensate
Nozzles
Tube wall
Steam Tube Cross Section

## Slide 12: Product Overview
Atmospheric Installation
Atmospheric Steam
Trap and
Funnel

## Slide 13: Product Overview
Why Insulate?
Wasted energy - Lost heat is lost money
Wasted Water (Condensate)
Air stream heat gain
Low humidifier output
Low system efficiency
SAM-e Insulated Option

## Slide 14: Product Overview
Types of Insulation
Header Insulation
Tube Insulation

## Slide 15: Product Overview
Benefits of Insulation
Thermal Resistance,
R = 0.66 ft-ºF-hr/Btu
Up to 70% condensate reduction
120°F max surface temperature
Reduce heat gain
Improved efficiency
Saves money!

## Slide 16: Product Overview
Insulated Tube
Stainless steel
shielding
¼” Air-gap
Cool Airflow
Insulated Steam Tube Cross Section
Hot Steam

## Slide 17: Tube Performance
Chart: Duct Velocity (ft/min)
Condensate Losses per Linear Foot

## Slide 18: Header Performance
Chart: Duct Velocity (ft/min)
| 200 | 225 | 250 | 275 | 300 | 325 | 350 | 375 | 400 | 425 | 450 | 475 | 500 | 525 | 550 | 575 | 600 | 625 | 650 | 675 | 700 | 725 | 750 | 775 | 800 | 825 | 850 | 875 | 900 | 925 | 950 | 975 | 1825 | 1850 | 1875 | 1900 | 1925 | 1950 | 1975 | 2000 | 2025 | 2050 | 2075 | 2100 | 2125 | 2150 | 2175 | 2200 | 2225 | 2250 | 2275 | 2300 | 2325 | 2350 | 2375 | 2400 | 2425 | 2450 | 2475 | 2500
50°F Standard | 0.30657 | 0.32972 | 0.3519 | 0.37325 | 0.39387 | 0.41384 | 0.43324 | 0.45211 | 0.47051 | 0.48847 | 0.50603 | 0.52323 | 0.54008 | 0.55661 | 0.57284 | 0.5888 | 0.60449 | 0.61994 | 0.63514 | 0.65013 | 0.66491 | 0.67949 | 0.69387 | 0.70808 | 0.72211 | 0.73597 | 0.74968 | 0.76323 | 0.77663 | 0.78989 | 0.80302 | 0.81601 | 1.2594 | 1.2732 | 1.2871 | 1.3009 | 1.3146 | 1.3284 | 1.342 | 1.3557 | 1.3693 | 1.3829 | 1.3965 | 1.41 | 1.4235 | 1.437 | 1.4504 | 1.4638 | 1.4772 | 1.4905 | 1.5039 | 1.5171 | 1.5304 | 1.5436 | 1.5568 | 1.57 | 1.5832 | 1.5963 | 1.6094 | 1.6225
60°F Standard | 0.287 | 0.30867 | 0.32944 | 0.34943 | 0.36873 | 0.38743 | 0.40559 | 0.42325 | 0.44048 | 0.45729 | 0.47373 | 0.48983 | 0.50561 | 0.52108 | 0.53628 | 0.55122 | 0.56591 | 0.58037 | 0.59461 | 0.60864 | 0.62247 | 0.63612 | 0.64959 | 0.66288 | 0.67602 | 0.689 | 0.70183 | 0.71451 | 0.72706 | 0.73948 | 0.75177 | 0.76393 | 1.1755 | 1.1884 | 1.2013 | 1.2142 | 1.227 | 1.2398 | 1.2526 | 1.2654 | 1.2781 | 1.2908 | 1.3034 | 1.3161 | 1.3287 | 1.3412 | 1.3538 | 1.3663 | 1.3788 | 1.3912 | 1.4037 | 1.4161 | 1.4284 | 1.4408 | 1.4531 | 1.4654 | 1.4777 | 1.4899 | 1.5022 | 1.5144
70°F Standard | 0.26753 | 0.28773 | 0.30708 | 0.32571 | 0.34371 | 0.36114 | 0.37806 | 0.39453 | 0.41058 | 0.42626 | 0.44159 | 0.45659 | 0.4713 | 0.48572 | 0.49989 | 0.51381 | 0.52751 | 0.54098 | 0.55426 | 0.56734 | 0.58023 | 0.59295 | 0.60551 | 0.6179 | 0.63014 | 0.64224 | 0.6542 | 0.66603 | 0.67772 | 0.6893 | 0.70075 | 0.71209 | 1.0924 | 1.1045 | 1.1165 | 1.1284 | 1.1404 | 1.1523 | 1.1642 | 1.176 | 1.1878 | 1.1996 | 1.2114 | 1.2231 | 1.2348 | 1.2465 | 1.2582 | 1.2698 | 1.2814 | 1.293 | 1.3045 | 1.316 | 1.3275 | 1.339 | 1.3505 | 1.3619 | 1.3733 | 1.3847 | 1.3961 | 1.4074
80°F Standard | 0.24832 | 0.26707 | 0.28504 | 0.30233 | 0.31903 | 0.33521 | 0.35092 | 0.36621 | 0.38111 | 0.39566 | 0.40988 | 0.42381 | 0.43746 | 0.45085 | 0.464 | 0.47693 | 0.48964 | 0.50215 | 0.51447 | 0.52661 | 0.53858 | 0.55038 | 0.56204 | 0.57354 | 0.58491 | 0.59614 | 0.60724 | 0.61821 | 0.62907 | 0.63981 | 0.65044 | 0.66097 | 1.012 | 1.0232 | 1.0343 | 1.0454 | 1.0564 | 1.0675 | 1.0785 | 1.0894 | 1.1004 | 1.1113 | 1.1222 | 1.1331 | 1.1439 | 1.1547 | 1.1655 | 1.1763 | 1.1871 | 1.1978 | 1.2085 | 1.2192 | 1.2298 | 1.2405 | 1.2511 | 1.2617 | 1.2722 | 1.2828 | 1.2933 | 1.3038
50°F Insulated | 0.23545 | 0.24532 | 0.25429 | 0.26238 | 0.26994 | 0.27695 | 0.28336 | 0.28946 | 0.29518 | 0.30046 | 0.30554 | 0.31025 | 0.31471 | 0.31906 | 0.32309 | 0.32705 | 0.33072 | 0.33424 | 0.33761 | 0.34095 | 0.34405 | 0.34704 | 0.35002 | 0.3528 | 0.35547 | 0.35805 | 0.36066 | 0.36307 | 0.36541 | 0.36767 | 0.36987 | 0.37211 | 0.43319 | 0.4344 | 0.43559 | 0.43676 | 0.43791 | 0.43904 | 0.44014 | 0.44144 | 0.44251 | 0.44356 | 0.4446 | 0.44561 | 0.44661 | 0.44759 | 0.44856 | 0.44951 | 0.45045 | 0.45137 | 0.45247 | 0.45337 | 0.45424 | 0.45511 | 0.45596 | 0.4568 | 0.45762 | 0.45844 | 0.45924 | 0.46003
60°F Insulated | 0.22053 | 0.22979 | 0.23819 | 0.24589 | 0.25287 | 0.25944 | 0.26556 | 0.27118 | 0.27654 | 0.28149 | 0.28616 | 0.29068 | 0.29487 | 0.29895 | 0.30273 | 0.30634 | 0.30989 | 0.31319 | 0.31636 | 0.31949 | 0.32241 | 0.32521 | 0.32791 | 0.33061 | 0.33312 | 0.33554 | 0.33789 | 0.34016 | 0.34245 | 0.34458 | 0.34664 | 0.34864 | 0.40543 | 0.40657 | 0.4077 | 0.4088 | 0.40988 | 0.41114 | 0.41218 | 0.41321 | 0.41422 | 0.41521 | 0.41618 | 0.41714 | 0.41808 | 0.41901 | 0.41992 | 0.42081 | 0.4217 | 0.42275 | 0.42361 | 0.42445 | 0.42527 | 0.42609 | 0.42689 | 0.42768 | 0.42846 | 0.42923 | 0.42999 | 0.43073
70°F Insulated | 0.20567 | 0.21431 | 0.22215 | 0.22934 | 0.23586 | 0.242 | 0.24771 | 0.25295 | 0.25797 | 0.26259 | 0.26695 | 0.27117 | 0.27508 | 0.2789 | 0.28243 | 0.28581 | 0.28903 | 0.29221 | 0.29516 | 0.298 | 0.30072 | 0.30343 | 0.30596 | 0.30839 | 0.31074 | 0.3131 | 0.31529 | 0.31741 | 0.31946 | 0.32145 | 0.32347 | 0.32534 | 0.37784 | 0.37891 | 0.37997 | 0.38118 | 0.3822 | 0.38319 | 0.38417 | 0.38513 | 0.38608 | 0.38701 | 0.38792 | 0.38882 | 0.38971 | 0.39058 | 0.39143 | 0.39244 | 0.39327 | 0.39408 | 0.39489 | 0.39568 | 0.39645 | 0.39722 | 0.39797 | 0.39872 | 0.39945 | 0.40017 | 0.40088 | 0.40158
80°F Insulated | 0.19094 | 0.19896 | 0.20617 | 0.21284 | 0.21899 | 0.22461 | 0.22991 | 0.23479 | 0.23945 | 0.24375 | 0.2478 | 0.25172 | 0.25536 | 0.25881 | 0.26219 | 0.26533 | 0.26832 | 0.27119 | 0.27403 | 0.27666 | 0.27919 | 0.28163 | 0.28406 | 0.28633 | 0.28851 | 0.29062 | 0.29265 | 0.29471 | 0.29662 | 0.29847 | 0.30026 | 0.302 | 0.35055 | 0.35156 | 0.35254 | 0.3535 | 0.35445 | 0.35538 | 0.35629 | 0.35719 | 0.35808 | 0.35894 | 0.3598 | 0.36064 | 0.36146 | 0.36243 | 0.36323 | 0.36402 | 0.36479 | 0.36555 | 0.3663 | 0.36704 | 0.36776 | 0.36848 | 0.36918 | 0.36988 | 0.37056 | 0.37123 | 0.3719 | 0.37255
Condensate Losses per Linear Foot

## Slide 19: Installation
Condair SAM-e

## Slide 20: Installation
SAM-e Mounting Options
Header sits on duct floor
Mounting frame
Optional 12” or 20” support stands
In-Duct Mounting

## Slide 21: Installation
SAM-e Mounting Options
Mounting frame required
10 – 30° angle
Vertical Duct Mounting
10-30°

## Slide 22: Installation
SAM-e Accessories
Mounting Frame
Stand Kit
Insulation

## Slide 23: Features & Benefits
Short Absorption Manifold

## Slide 24: Features & Benefits
304 Stainless Steel parts
  Less Maintenance
10 years warranty
OSHPD Certified

## Slide 25: Mini SAM-e
Condair Mini SAM-e

## Slide 26: Mini SAM-e
Mini SAM-e
For ducts 12” x 8” to 24” x 24”
Horizontal flow standard
Vertical flow as special
Capacities up to 210 lbs/hr

## Slide 27: Mini SAM-e Steam Tubes
Mini SAM-e Steam Tubes
Lengths from 5” to 21”
3 Types:
Type MA: 10 lbs/hr
Type MB: 20 lbs/hr
Type MC: 30 lbs/hr
Length

## Slide 28: Insulated Mini SAM-e
Insulated Mini SAM-e
Header Insulation
Tube Insulation

## Slide 29: Installation
Place header on duct floor
Install steam tubes with insertion stop washers

## Slide 30: Single Tube Distributor
xSD (ASD, BSD, CSD)

## Slide 31: Single Tube Distributor (xSD)
Type of Tubes Tubes
  Steam Distributor (A-B-CSD)
Type | Max output (lbs/hr) | Min Duct width (in) | Max duct width (in) | Min duct height (in)
ASD | 25 | 10 | 66 | 8
BSD | 35 | 10 | 102 | 10
CSD | 115 | 24 | 144 | 14
Distributor Nozzle | 8 | 8 | None | 8

## Slide 32: Installation
Mounting Distributors Tubes
Mount Level
5/16” UNC Threaded Rod and Nut (by Others)
L Bracket by Others
*Support rod mandatory for distributors longer than 36” (915mm)

## Slide 33: Installation
Steam Distributors Tubes
WRONG!
*Steam distributors must be mounted level

## Slide 34: Installation
Steam Distributors Tubes - Clearances
H
1/3 H
2/3 H
H
B
A
W
2/3 W
1/3 W
W
1/2 W
1/2 W
Horizontal Airflow
Vertical Airflow
* Min. W = 8” (203mm)
Distributor | H Min. | A | B
ASD | 8” | 5” | 3”
BSD | 10” | 6” | 4”
CSD | 14” | 9” | 5”

## Slide 35: Installation
Steam Distributors Tubes
1
2
3
  Vertical Duct Applications

## Slide 36: Installation
Steam Distributors Tubes - Installation
H
B
B
A
B
Distributor | H Min. | A | B
ASD | 18” | 3” | 5”
BSD | 22” | 4” | 6”
CSD | 32” | 5” | 9”
Steam Header
*Steam Header or Splitting Manifolds recommended for even steam distribution

## Slide 37: Installation
Steam Distributors Tubes - Clearances
Abs. Dist x 2
6
'
M
i
n
.
Mount steam distributor at least 6’ (2m) downstream from elbow
Multiple distributors can reduce this distance
  In Duct Near an Elbow

## Slide 38: Installation
Steam Distributors Tubes - Location
B
r
a
n
c
h
D
u
c
t
D
r
a
i
n
P
a
n
D
r
a
i
n
P
a
n
To Drain
The Mini SAM-e is a great alternative for these situations!

## Slide 39: Installation
Steam Distributors Tubes - Location
  Air Handling Unit

## Slide 40: Installation
Steam Distributors Tubes - Location
  Air Handling Unit
LOCATION ADVANTAGE DISADVANTAGE
LOC. 1 MOST recommended.
Assuming there is sufficient High velocity may create long absorption
  straight duct for absorption. distances.

## Slide 41: Installation
Steam Distributors Tubes - Location
  Air Handling Unit
LOCATION ADVANTAGE DISADVANTAGE
LOC. 2 Warm air. Any unabsorbed steam may condense on the coils.
Good absorption. Capacity drop due to eventual condensation on the
coils.

## Slide 42: Installation
Steam Distributors Tubes - Location
  Air Handling Unit
LOCATION ADVANTAGE DISADVANTAGE
LOC. 3 Warm air. If absorption distance is too long it may damage the fan

## Slide 43: Installation
Steam Distributors Tubes - Location
  Air Handling Unit
LOCATION ADVANTAGE DISADVANTAGE
LOC. 4 Heating coils help evaporate Absorption may be a problem due to low mixing temperatures
Air is mixed well Cold Air, No drain pan on coil

## Slide 44: Installation
Steam Distributors Tubes - Location
  Air Handling Unit
LOCATION ADVANTAGE DISADVANTAGE
LOC. 5 Not recommended Filters may get wet and saturated
Cold Air

## Slide 45: Installation
Steam Distributors Tubes - Location
  Air Handling Unit
LOCATION ADVANTAGE DISADVANTAGE
LOC. 6 Not recommended Outside air may cause condensate problems
Problematic RH control

## Slide 46: Steam Line Rules
Main Rules for Atmospheric Steam lines
Follow recommended materials, size and length
Always Insulate with 1” pipe insulation
Slope the steam lines
Trap condensate

## Slide 47: Steam Line Rules
Recommended Materials for Steam lines
Model | Steam Line |  |  | 
 | Maximum Equivalent Length | MED-L Copper Pipe Diameter | Stainless Steel Pipe Diameter | Steam Losses***
EL005 | 7 ft (2 m) | ¾ in (20 mm) | ⅞ in x 0.049 wall (22 mm x 1.25 mm wall) | 0.06 lb/h/ft (0.09 kg/h/m)
EL010 | 12 ft (3.5 m) |  |  | 
EL020 | 17 ft (5 m) |  |  | 
EL030 | 22 ft (6.5 m) |  |  | 
EL050 | 43 ft (13 m) | 1-1/2 in (40 mm) | 1¾ in x 0.065 wall (45 mm x 1.65 mm wall) | 0.11 lb/h/ft (0.18 kg/h/m)
EL075 EL100 | 47 ft (14 m) |  |  | 
EL150* EL200* | 50 ft (15 m) |  |  | 
* Use a single steam line for each steam cylinder. Do not combine lines except at a distributor, and only if using the humidifiers in parallel. *** Based on 1 in (25 mm) insulated copper. |  |  |  | 
DI water requires Stainless steel steam lines!

## Slide 48: Steam Line Rules
Recommended Materials for Steam lines
Model | Over-sized Steam Line** |  |  | 
 | Maximum Equivalent Length | MED-L Copper Pipe Diameter | Stainless Steel Pipe Diameter | Steam Losses***
EL005 | 14 ft (4 m) | 1 in (25 mm) | 1⅛ in x 0.049 wall (29 mm x 1.25 mm wall) | 0.06 lb/h/ft (0.09 kg/h/m)
EL010 | 24 ft (7 m) |  |  | 
EL020 | 34 ft (10 m) |  |  | 
EL030 | 44 ft (13 m) |  |  | 
EL050 | 86 ft (26 m) | 2 in (50 mm) | 2 in x 0.065 wall (50 mm x 1.65 mm wall) | 0.11 lb/h/ft (0.18 kg/h/m)
EL075 EL100 | 94 ft (28 m) |  |  | 
EL150* EL200* | 100 ft (30 m) |  |  | 
* Use a single steam line for each steam cylinder. Do not combine lines except at a distributor, and only if using the humidifiers in parallel. ** The over-sized lines may require a reducer at the humidifier and the steam distributor. |  |  |  | 

## Slide 49: Steam Line Rules
Equivalent Lengths
Nominal Tube Diameter, inches | Standard 90 degree Elbow | Standard 45 degree Elbow | Side Outlet Tee
¾” – 7/8” | 2 ft | 1 ft | 4ft
1 ½” – 1 ¾” | 3.5 ft | 1.75 ft | 7 ft
3” | 5 ft | 2.5 ft | 11 ft
4” | 8 ft | 4 ft | 15 ft
*Valve in full open position |  |  | 

## Slide 50: Steam Line Rules
Rule # 1
1) Always install at least 12” of vertical run directly from the humidifier before any slope or bend occurs.
  *Condensate returned to
  Unit or drain
  *Condensate should not be routed back to a sink used frequently
  by personnel.

## Slide 51: Steam Line Rules
Rule # 2
2) For upward slopes in steam lines, minimum allowable slope is 10 degrees grade (2” vertically up per 12” horizontal run)
  2”
  12”

## Slide 52: Steam Line Rules
  12”
  0.5”
Rule # 3
3) For downward slopes in steam lines, minimum allowable slope is 2 degrees grade (0.5” vertically down per 12” horizontal run).

## Slide 53: Steam Line Rules
Rule # 4
4) Always ensure a minimum bend radius of 12” when using flexible steam hoses or 5 times the internal diameter for rigid steam lines.

## Slide 54: Steam Line Rules
Rule # 4.5
4.5) When using Nortec steam hose, ensure line is properly supported

## Slide 55: Steam Line Rules
Rule # 5
5) When supplying a single distributor by multiple humidifiers, always run separate steam lines for the entire run. Connect the steam lines by a Nortec Adapter Box at the distributor. Never connect lines on an upward slope.

## Slide 56: Steam Line Rules
Where to Use Condensate Traps
As a minimum guideline, condensate traps must be installed along the steam line for each of the following scenarios: a. At the base of a horizontal to vertical transition. b. At any low point along the steam line. c. After a length of steam line run 15 feet or greater.

## Slide 57: Steam Line Rules
Condensate Traps
12” drop to top of P-trap
  Full Size Tee Condensate Trap
  Copper Tee
  Cap
  Condensate Line
8” or Duct S.P. + 2”

## Slide 58: Steam Line Rules
Horizontal to Vertical Transitions

## Slide 59: Steam Line Rules
Horizontal to Vertical Transitions
  Full Size Copper Tee
  Condensate Drain

## Slide 60: Steam Line Rules
Place the Condensate Trap
  6 ft.
  17 ft.
  5 ft.
  1 ft.

## Slide 61: Key Takeaways
SAM-e comes with 10 years warranty
Can be used for Atmospheric and pressurized steam
OSHPD (Seismic) certified

## Slide 62: Questions?

## Slide 63: Time for a Break!!!