## Slide 1: Humidity 101
Stanley Tom & Marlee Spiegelberg

## Slide 2: Outline/Agenda
Humidity 101
Why Buildings Get Dry
Dryness and Seasonality
Dryness in Process
Dryness and People
The Latest in Humidity Research
Practical Humidity Control

## Slide 3: Humidity 101
Relative Humidity is relative to temperature (%)
1 lb (0.5 kg) Air
35°F (2°C)
30 gr (2g/kg)
100% RH
Sensible Heating
Absolute Humidity is measured by mass (gr/lb, g/kg)
1 lb (0.5 kg) Air
72°F (22°C)
30 gr (2g/kg)
25% RH

## Slide 4: Humidity vs. Temperature
35°F
(2°C)
72°F
(22°C)
120°F
(49°C)
Temperature
25% RH
Absolute Humidity
30 gr (2g/kg)
120 gr (8g/kg)
100% RH

## Slide 5: The Psychometric Chart

## Slide 6: What Causes Dryness?
Outside air with low absolute humidity dries building
Image: Free Stock Photos 14413
Outside Air
6°F (-14°C)
53% RH
4 gr/lb (0.6 g/kg)
Inside Air
70°F (21°C)
4% RH
4 gr/lb (0.6 g/kg)
Ventilation
In/Exfiltration
Sensible Heating

## Slide 7: Seasonal Dryness: Fixed Air Volume Ventilation Example
September
January
December
October
April
March
November
February
May
June
July
August
Indoor
Dryness
Indoor
Dampness

## Slide 8: Is Dryness A Problem?
Licensed from www.peopleimages.com
iStock: 000030384618X
Occupant Health and Wellness
Manufacturing and Processes

## Slide 9: Manufacturing and Process
Hygroscopic
Materials
Evaporation
Rates
Static
Charges

## Slide 10: Evaporation Rates and Drying
iStock: 000002955937
Vapor pressure differential drives moisture flow
Quality concerns:
  Water based sprays / paint
  Shrinkage
  Adhesion
  Runs / Drips

## Slide 11: Hygroscopic Materials
iStock Images
Moisture absorbs/desorbs in hygroscopic materials
Quality concerns:
  Dimensional instability
  Cracking / deterioration
  Coating delamination
Examples
  Printing
  Building Finishes
Animation Courtesy Condair Group AG

## Slide 12: Static Electricity
Moisture provides conductive path for electrons
Quality concerns:
  Component damage
  Static cling
  Unpredictable spray pattern
  Paint Defects
  Ignition of volatile compounds
iStock: 000002955937
1 Graham Hearn, Wolfson Electrostatics, Controlling Static Electricity in Modern Buildings
1

## Slide 13: Humidity and Building Occupants

## Slide 14: Occupant Health and Wellness
Human Body Response
  Human body is ~60% water
  Body doesn’t sense moisture well
Ambient Humidity Affects:
  Eyes
  Skin
  Throat
  Nose
  Hydration
  Immune System

## Slide 15: Human Body: Eyes
Our Eyes
  Protected by thin tear film
  Dry air causes increased desiccation
  Compounded by computer use
  Discomfort increases with time if dew point is below 26°F [1]
Typical Symptoms
  Eye discomfort
  Redness
  Photosensitivity
  1 J.E. Laviana, F.H. Rohles, Jr. and P.E. Bullock, Humidity Comfort and Contact Lenses (ASHRAE, 1988) 94(1), 3-11.
Chart: Eye Comfort Range
| 17.5 | 19.5 | 21 | 22.5 | 23.5 | 25 | 26.5 | 28 | 30 | 32 | 34
Temperature {F} | 82.4 | 80.6 | 78.8 | 77 | 75.2 | 73.4 | 71.6 | 69.8 | 68 | 66.2 | 64.4

## Slide 16: Human Body: Skin
Our Skin
  Skin provides protection and thermal regulation
  Thermal regulation via evaporative cooling
  Dry environments disrupt moisture balance
    Increased evaporation rates
  Below 30% RH skin becomes dry [1]
Typical Symptoms
  Thermal discomfort
  Dryness of skin surface
  Inflammation / aggravation of skin conditions
1 Sunwoo Y, Physiological and Subjective Responses to Low Relative Humidity in Young and Elderly Men, (J Physio Anthropol, 2006 May), 25(3):229-38.

## Slide 17: Human Body: Throat
Our Throat
  Provides channel for air to enter lungs
  Conditions air we breathe
  Dry air draws requires more moisture
Typical Symptoms
  Increased need to swallow
  Vocal chord irritation[1]
  1 National Institute on Deafness and Other Communication Disorders, Taking Care of Your Voice, https://www.nidcd.nih.gov/health/taking-care-your-voice (December 14, 2016)
  US National Institute of Health recommends >30% RH + drinking water

## Slide 18: Human Body: Hydration
Our Body and Brain
  Rely on water for many processes
  Brain is ~85% water
  Dry environments increase water loss
Possible Symptoms
  Decreased cognitive function at 2% dehydrated
  Reduced short term memory
  Increased fatigue and moodiness
https://www.usgs.gov/special-topics/water-science-school/science/water-you-water-and-human-body

## Slide 19: Fraunhofer Study: Air Humidity in the Office Workplace (2014)
“Air humidity at the workplace can thus be assessed as a building block for increasing a person's well-being and for possibly reducing health risks.” [1]
  Reduced eye strain
  Reduced vocal strain
  Reduced allergy and asthma impact
  Increased employee performance
  Mental acuity
  Improved perceived comfort (“humidex”)
[1] Rief S and Juric M, Air Humidity in the Office Workplace, Fraunhofer IAO, 2014
Research started with occupant surveys via internet
Experiment related to “I feel air is often too dry”
  No Humidifier, Placebo Humidifier, Active Humidifier

## Slide 20: What Does ASHRAE Say?
ASHRAE Standard 55
  “There are no established lower level humidity limits for thermal comfort, consequently, this standard does not specify a minimum humidity level. NOTE: Non-thermal comfort factors such as skin drying, irritation of mucous membranes, dryness of the eyes, and static electricity generation may place limits of the acceptability of very low humidity environments.”
The Sterling Chart
  Common design reference
  Optimal mid-range 40 - 60%

## Slide 21: ASHRAE Research Project 1630
“Update of the Scientific Evidence for Specifying Lower Limit Relative Humidity Levels for Comfort, Health and IEQ in Occupied Spaces”
Literature Review: 600 articles of interest, 70 detailed reviews
Focused on comfort, health, and IEQ
Findings consistent with Sterling Chart in ASHRAE Handbook
  Lower humidity decreased house dust mite allergens
  Lower humidity increased virus survival for influenza
  Health, comfort, skin dryness, eye irritation, and static electricity increased as humidity decreased
Low and High humidity control is important for comfort, wellness, and health

## Slide 22: Humidity and Health: Research
Humidity and Respiratory Infections
  Evidence of link between moisture and cold / flu transmission
  Clinical trials between 1963 and 1985 showed significant reduction of respiratory infections when mid-range humidity was maintained [1-5]
1. Ritzel G, Sozialmedizinische Erhebung zur Pathogenese und Prophylaxe von Erkältungskrankheiten, sog. «Kindergartenstudie» Zeitschrift für Präventivmedizin 1966, 11. 9-16
2. Sale C, Humidification to Reduce Respiratory Illnesses in Nursery School Children, Southern Medical Journal, July 1972, Vol 65
3. Green G H, Winter humidity and related absenteeism in Canadian hospitals, Digest of the 3rd. CMBES
4. Green G H, The effect of indoor relative humidity on absenteeism and colds in schools, ASHRAE Trans., Vol. 80, Part II
5. Gelperin A, Humidification and upper respiratory infection incidence, Heating, Piping and Air Conditioning, 45:3, 1973

## Slide 23: Humidity and Health: Seasonality of Influenza
1 https://www.cdc.gov/flu/about/season/flu-season.htm

## Slide 24: Humidity and Health: Seasonality of Influenza
Why?[1]
More time indoors in proximity to others
Drying of nasal mucous membrane weakens respiratory system
Influenza virus is most stable at lower RH[2]
Exhaled aerosols float longer in lower humidity
1 Anice Lowen, et al, Influenza Virus Transmission Is Dependent on Relative Humidity and Temperature (October 19, 2007)
2J. Metz, et al, Influenza and Humidity – Why a bit more damp may be good for you! (June 2015)

## Slide 25: 2010 CDC Funded Study on SARS-CoV Coronavirus Survival
https://www.ncbi.nlm.nih.gov/pmc/articles/PMC2863430/
“”there was greater survival or a greater protective effect [for the virus] at low RH (20%) and high RH (80%) than at moderate RH (50%).”
“Greater survival of other enveloped viruses, including vaccinia virus, Venezuelan equine encephalitis virus, and influenza virus, at low RH has been observed previously (11, 12, 13, 26, 27).”
“…maximum rates of Maillard reactions
occur when the RH is 50 to 80%) (9), possibly providing a partial explanation for why viral inactivation appears to be more rapid at 50% RH than at 20% or 80% RH.”

## Slide 26: Infectious Particles: NIOSH/CDC Simulated Cough Experiment
100μm
50μm
<5μm
Travel Distance
Droplet Size
1m
10+m
[1] Noti JD et. al, High Humidity Leads to Loss of Infectious Influenza Virus from Simulated Coughs, PLoS ONE 8(2): e57485, 2013
Infectious payloads travel farther
Particles lose mass quickly in dry environment
Smaller light particles fly farther (0.5 µm particles float up to 41 hours)
Influenza Infectivity is retained[1]

## Slide 27: Infections: Research in LEED Silver Hospital
Room environment vs. patient infection rates
Microbiome study in a new LEED Silver hospital in the USA
240 single-occupancy inpatient rooms
52 ICU beds. 28 operating suites
A three layer study over 13 months
10 monitored patient rooms (300 patients)
9 continuously measured parameters (Room ach, visitor traffic, outdoor air factions, room pressure, temperature, absolute humidity, relative humidity, CO2, air pressure, lux) ~8 million data points
Image Courtesy Dr. Stephanie Taylor
Hygiene and sanitization have gotten better, why have HAI rates not improved?

## Slide 28: Infections: Research in LEED Silver Hospital
Results: 15% of Patients contracted a “Healthcare Acquired Infection” (HAI)

## Slide 29: Infections: Research in LEED Silver Hospital - Results
Chart: 
| Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Healthcare-Associated Infections in 10 monitored patient rooms | 9 | 7 | 6 | 5 | 1 | 1 | 0 | 2 | 4 | 3 | 7
Avg RH for all patient rooms | 31.8 | 31.6 | 33.5 | 39 | 41.5 | 41.3 | 41.6 | 37.5 | 31.6 | 32.5 | 32.2
Indoor
Relative Humidity
Healthcare-Associated
Infections
As relative humidity decreased infection rates increased
Confidence: (t < 0.02)
Adapted from Source: Colonization and Succession of Hospital-Associated Microbiota [Restyled for readability] Simon Lax, Daniel Smith, Naseer Sangwan, Kim Handley, Peter Larsen, Miles Richardson, Stephanie Taylor, Emily Landon, John Alverdy, Jeffrey Siegel, Brent Stephens, Rob Knight, Jack A Gilbert

## Slide 30: Research in a School: “Humidity as a Non-Pharmaceutical Intervention for Influenza A”
[1] J. Reiman et al, Humidity as a non-pharmaceutical intervention for influenza A, 2018 https://journals.plos.org/plosone/article?id=10.1371/journal.pone.0204337
Research builds upon NIOSH/CDC and microbiome research
Focused on preschool classrooms
Air and toy samples processed with PCR looking for influenza A
Compared standard rooms with rooms where humidity control was added
Hypothesis: “…raising absolute humidity above seasonal lows would impact influenza virus survival and transmission in a key source of influenza virus distribution, a community school.”
Photo Credit: iStock 34019410

## Slide 31: Research in a School: “Humidity as a Non-Pharmaceutical Intervention for Influenza A”
Results:
“There were 2.3 times as many ILI [influenza like illness] cases in the control rooms compared to the humidified rooms…”
“… whether there is a causal relationship, and its direction between the number of cases and levels of influenza virus in the rooms is not known.”
“Additional research is required, but this is the first prospective study suggesting that exogenous humidification could serve as a scalable NPI for influenza or other viral outbreaks.”
[1] J. Reiman et al, Humidity as a non-pharmaceutical intervention for influenza A, 2018 https://journals.plos.org/plosone/article?id=10.1371/journal.pone.0204337
%RH in classrooms | % Airborne particles carrying virus (PCR) | Virulence of airborne virus | # children absent due to influenza like illness
20% | 49% | 75% | 22
45% | 19% | 35% | 9

## Slide 32: 2019: Research of How Humidity Affects Immune System
Results:
Low humidity environments made mice more susceptible to infection
Mechanisms were related to cilia, mucous, and lung tissue function
“These results indicate that exposure to dry air impairs host defense against influenza infection, reduces tissue repair, and inflicts caspase-dependent disease pathology.”
[1] Kudo et al, Low ambient humidity impairs barrier function and innate resistance against influenza infection
Proceedings of the National Academy of Sciences May 2019, 116 (22) 10905-10910; DOI: 10.1073/pnas.1902840116
https://www.pnas.org/content/116/22/10905
Studied immune response in mice:
Likelihood of acquiring infection
Mucocilioary performance
Lung tissue response and tissue repair

## Slide 33: 2022: Covid 19 Aerosol Loading
Results:
Increased ventilation and filtration significantly reduced aerosol and surface viral loads
Higher humidity resulted in lower aerosol and higher surface viral load due to increased rate of particle deposition at higher relative humidity
“The findings indicate that building operation practices such as ventilation, filtration, and humidification substantially reduce the environmental aerosol viral load and therefore inhalation dose, and should be prioritized to improve building health and safety.”
[1] Hooman Parhizkar, Leslie Dietz, Andreas Olsen-Martinez, Patrick F Horve, Liliana Barnatan, Dale Northcutt, Kevin G Van Den Wymelenberg, Quantifying Environmental Mitigation of Aerosol Viral Load in a Controlled Chamber With Participants Diagnosed With Coronavirus Disease 2019, Clinical Infectious Diseases, 2022; ciac006, https://doi.org/10.1093/cid/ciac006
Studied effects of environment conditions on aerosol loading:
11 students diagnosed with Covid-19
Each spent 3 days in controlled chamber
Varied ventilation, filtration, humidity

## Slide 34: Human Body: Nose / Immune System
Our Nose/ Immune System
  Mucous membrane and cilia filter we breathe
  Capture and drain infectious particles
  Dry environments desiccate and thicken mucous[1]
Possible Issues
  Reduced cilia motion
  Reduced ability for mucous to drain
  Increased risk of infection
1 J.P. Guggenbichler, R. Huster and S. Geiger, Luftfeuchtigkeit und Immunabwehr
Die Rolle der Schleimhaut und Auswirkungen auf die Klimatechnik (2007) Tab Technik AM, Vol. 38, No. 9

## Slide 35: It Is Time to Rethink Indoor Environments
low RH intermediate RH high RH
low wa water activity (wa) high wa
  WE
  THOUGHT
keeping buildings dry is a
strategy for eliminating
microbes and preventing
health problems
WE KNOW
Dampness creates conditions favorable to mold
Mid-range RH
Supports health!

## Slide 36: COVID-19: New Guidance at Home and Long Term Care
https://www.canada.ca/en/public-health/services/diseases/2019-novel-coronavirus-infection/guidance-documents/guide-home-ventilation-covid-19-pandemic.html
https://www.canada.ca/en/public-health/services/diseases/2019-novel-coronavirus-infection/guidance-documents/guide-ltch-ventilation-covid-19-pandemic.html
“While humidifiers do not remove SARS-CoV-2 virus from the indoor air environment, they could impact the duration that particles that contain virus are suspended in the air, and how long they remain infectious. It is therefore important to maintain an optimal humidity level, between 30% and 50% in indoor settings.”

## Slide 37: Temperature, Humidity, CO2: Simple Tools for Healthy Buildings
Parameter | Parameter | Optimal | Rationale
 | Temperature | 20°C – 23°C | Thermal comfort Minimize environmental stress for occupants
 | Relative Humidity | 40 – 60% | Health / immune system support Reduce particle float time Reduce particle infectiousness
 | Carbon Dioxide | 800 – 1000 ppm (Maximum) | Surrogate for exhaled particles Baseline 400 ppm Exhaled air ~40,000ppm +400 ppm ~ 1% of exhaled air

## Slide 38: Temperature, Humidity, CO2 in Practice
Feeling very safe
In Zürich Airport!
In flight: it’s gotten
better
On approach: values
rise again
In aircraft:
boarding completed…

## Slide 39: Humidity Targets
Photo Credit: iStock 000018649460
For People:
40 – 60% RH (Ideal)
Photo Credit: iStock 000022275438
For Process:
Varies with Process

## Slide 40: Humidity Control in Practice

## Slide 41: Practical Humidity : Adding Moisture to the Air
Water Vapor
Liquid Water
Heat of Evaporation:
970 – 1075 BTU/lb
2257 - 2500 kJ/kg
Steam: Energy comes from electricity, gas, or heat exchange process
Spray / Evaporative: Energy comes from the air
= SENSIBLE COOLING!

## Slide 42: Practical Humidity : Managing Energy
Humidification load is proportional to outside air volume
  Use minimum outside airflow when possible
  Caution with high performance standards that reward high ACH
  Use a set point of 40 - 45%
Use total energy (enthalpy) recovery wheels / plates
  Recover up to 70% of moisture in exhaust
  Bonus: Reduce dehumidification loads in summer
Be careful with airside economizer optimization
  Large quantities of cool outside air cause dryness
  Look at total enthalpy not just temperature

## Slide 43: Practical Humidity: …But What About Mold?
High wa + nutrient rich substrate = mold
Most organisms require wa > 0.7 with optimal conditions
Keys to Avoid Mold:
Avoid prolonged exposure of building to RH > 60%
Minimize localized areas of high %RH (air leaks, cold pipes, etc.)
Avoid condensation
Scott (1953 &1957): Water activity factor determines growth of mold
Water Activity Factor: A measure of the energy status of water in a system
[1]
[1]
[1] Carter, Brady. 2015. How Dry Am I? Presented at the 2015 ASHRAE Summer Conference, Atlanta, Georgia, June 28

## Slide 44: Practical Humidity : Avoiding Condensation
Fenestration, Exterior Walls, Pipes
Resources: ASHRAE Journal Column: Building Sciences by Joe Lstiburek
Condensation occurs when humid air interacts with temperatures below the dew point
Strategies:
Cold temperature setback: 45% → 30%
Condensation sensors
Ventilate / supplemental heat for glass
Focus on quality in construction / vapor barriers
Image Credit: creativity103.com, Cropped

## Slide 45: Conclusion: Defeating Dryness and Getting Humidity Right
Buildings dry out when outside is drier than target levels
Humidity affects processes
Humidity affects occupant health
Optimum indoor range for occupants: 40 – 60% RH (and 20°C – 23°C, <1000 ppm)
Planning for humidity helps achieve great results

## Slide 46: Want To Learn More?
ASHRAE TC 5.11 - Humidifiers
  www.ashrae.org/
  www.ashrae.org/joinatc - Join by web call!
ASHRAE Resources
  Humidity IS Health (ASHRAE Bookstore)
  Putting People First: The Healing Power of Indoor Air (ASHRAE Virtual Conference)
  2020 Systems and Equipment Handbook Chapter 22
  Position Document on Airborne Infectious Diseases
©ASHRAE, www.ashrae.org
AHRI Free Education Resources
  Archived AHR Expo Presentations
  Other helpful resources
  ahrinet.org/humidifiers
Photo Credit: W. Truong
Photo Credit: J. Kane

## Slide 47: Thank you!